| METAL CABLE CO. DATA SHEET |  |  |  |  |
| --- | --- | --- | --- | --- |
| No.: MC – 18042 |  |  | Date : 95.10.19 |  |
| Low voltage power cable Acc. IEC 60502-1( ISIRI 3569-1) , (0.6/1)1.2 kv , frequency : 50 Hz |  |  |  |  |
| Copper conductor/ XLPE insulated/ pvc bedding/ galvanized steel wire armour/ pvc outer sheath Cable code : N2XRY-O |  |  |  |  |
| R | SPECIFICATION |  |  |  |
| 1 | Cable size |  |  | 7x1.5mm2 |
| 2 | Conductor | material |  | Plain annealed copper |
|  |  | Class |  | 2 , round |
|  |  | construction |  | 7x0.53 mm |
| 3 | Insulation | material |  | XLPE |
|  |  | operation temp. |  | 90°C |
|  |  | thickness |  | 0.7 mm |
|  |  | colour |  | Red , yellow , black N: white |
| 4 | Bedding | material |  | PVC |
|  |  | operation temp. |  | 90°C |
|  |  | thickness |  | 1.0 mm |
|  |  | colour |  | Black |
| 5 | Armour | material |  | Galvanized steel |
|  |  | type |  | Wire armour (GSWA ) |
|  |  | diameter |  | 1.2 mm |
| 6 | Outer jacket | material |  | PVC |
|  |  | operation temp. |  | 90°C |
|  |  | thickness |  | 1.8 mm |
|  |  | colour |  | Black |
| 7 | Overall diameter approx. |  |  | 17.0 mm |
| 8 | Max. dc conductor resistance at 20°C |  |  | 7.41 Ω/km acc. IEC 60228 |
| 9 | Max. ac conductor resistance at 90°C |  |  | 9.49 Ω/km |
| 10 | Min. Insulation resistance at 90 °C |  |  | 0.841 MΩ . km |
| 11 | Short circuit current |  |  | 0.357 kA at 1 second |
| 12 | High voltage test |  |  | 3.5 kvac or 8.4 kvdc for 5 min |
| 13 | Working temperature |  |  | -25 ____ +90 °C |
| 14 | Min. bending radius |  |  | 6 x D (Overall diameter) |
| 15 | Flame retardant test |  |  | As per IEC 60332-1 |
| 16 | Cable length (per drum) |  |  | 2000 M |
| 17 | Cable weight approx. |  |  | 620 kg/km |
| Marking : METAL CABLE CO. IEC 60502 N2XRY 7x1.5 SQMM 0.6/1 KV MADE IN IRAN 1395 |  |  |  |  |

Technical approval