| METAL CABLE CO. DATA SHEET |  |  |
| --- | --- | --- |
| No.: MC – 23519 |  | Date : 99.10.17 |
| Instrument cable Acc. BS EN 50288-7 , 500 V |  |  |
| Copper conductor/ XLPE insulated/ Ind. & Ove. screen (Alu. Foil)/ PVC bedding/ galvanized steel wire armour/ PVC outer sheath CU/XLPE/ISCR/OSCR/PVC/GSWA/PVC |  |  |
| Item | Specification |  |
| 1 | Cable size | 25x3x1.5 mm2 |
| 2 | Conductor material & construction | Plain annealed copper class 2 (7x0.53 mm) |
| 3 | Insulation thickness & material | 0.6 mm , XLPE/90 °C |
| 4 | Colour of insulation | White/ black/red with numbered |
| 5 | Max. lay of twist (triple) | 100 mm |
| 6 | Drain wire cross-section & material | 0.5 mm2 , tinned copper class 2 |
| 7 | Screen (individual & overall) | Aluminum – bonded polyester |
| 8 | Bedding thickness & material | 1.7 mm , PVC |
| 9 | Steel wire armour diameter | 2.0 mm |
| 10 | Jacket thickness & material | 2.3 mm , PVC , colour : blue |
| 11 | Overall diameter approx. | 47.8 mm |
| 12 | Max. dc conductor resistance at 20°C | 12.1 Ω/km acc. IEC 60228 |
| 13 | Max. ac conductor resistance at 90°C | 15.4 Ω/km |
| 14 | Min. Insulation resistance at 20 °C | 5000 MΩ . km |
| 15 | Max. mutual capacitance | 110 pf/m |
| 16 | Max. L/R | 40 µH/Ω |
| 17 | High voltage test | 1.0 kvac or 2.4 kvdc for 1 min |
| 18 | Working temperature | -25 ___ +90 °c |
| 19 | Min. bending radius | 8 x D (Overall diameter cable) |
| 20 | Flame retardant test | Acc. IEC 60332-1 |
| 21 | Cable length (per drum) | 500(1x500) M |
| 22 | Cable weight approx. | 3640 kg/km |
| Marking : METAL CABLE CO. BS EN 50288-7 CU/XLPE/ISCR/OSCR/PVC/GSWA/PVC 25x3x1.5 SQMM 300/500 V MADE IN IRAN 1399 |  |  |

Technical approval