| METAL CABLE CO. DATA SHEET |  |  |  |  |
| --- | --- | --- | --- | --- |
| No.: MC – 23524 |  |  |  | Date : 99.10.17 |
| Low voltage lead sheathed power cable Acc. IEC 60502-1 , (0.6/1)1.2 kv , frequency : 50 Hz |  |  |  |  |
| Copper conductor/XLPE insulated/PVC filler/lead sheathed/PVC bedding/steel wire armour/PVC outer sheath Cable code : N2XKYRY |  |  |  |  |
| R | SPECIFICATION |  |  |  |
| 1 | Cable size |  | 7x1.5 mm2 |  |
| 2 | Conductor | material | Plain annealed copper |  |
|  |  | Class | 2 , round |  |
|  |  | construction | 7x0.53 mm |  |
| 3 | Insulation | material | XLPE |  |
|  |  | operation temp. | 90°C |  |
|  |  | thickness | 0.7 mm |  |
|  |  | colour | Black with white numbered + Y/G |  |
| 4 | Filler - bedding | material | PVC |  |
|  |  | operation temp. | 90°C |  |
|  |  | thickness | 1.2 mm |  |
|  |  | colour | Black |  |
| 5 | Lead sheath | material | Lead alloy |  |
|  |  | thickness | 1.2 mm |  |
| 6 | Bedding | material | PVC |  |
|  |  | operation temp. | 90°C |  |
|  |  | thickness | 1.2 mm |  |
|  |  | colour | Black |  |
| 7 | Armour | material | Galvanized Steel |  |
|  |  | type | Wire armour ( GSWA ) |  |
|  |  | diameter | 1.25 mm |  |
| 8 | Outer jacket | material | PVC |  |
|  |  | operation temp. | 90°C |  |
|  |  | thickness | 1.8 mm |  |
|  |  | colour | Black |  |
| 9 | Overall diameter approx. |  | 22.8 mm |  |
| 10 | Max. dc conductor resistance at 20°C |  | 12.1 Ω/km acc. IEC 60228 |  |
| 11 | Max. ac conductor resistance at 90°C |  | 15.4 Ω/km |  |
| 12 | Min. Insulation resistance at 90 °C |  | 1.112 MΩ . km |  |
| 13 | Short circuit current |  | 0.214 kA at 1 second |  |
| 14 | High voltage test |  | 3.5 kvac or 8.4 kvdc for 5 min |  |
| 15 | Working temperature |  | -25 ____ +90 °C |  |
| 16 | Min. bending radius |  | 8 x D (Overall diameter) |  |
| 17 | Flame retardant test |  | Acc. IEC 60332-1 |  |
| 18 | Cable length (per drum) |  | 2000(1x2000) M |  |
| 19 | Cable weight approx. |  | 1355 kg/km |  |
| Marking : METAL CABLE CO. IEC 60502-1 N2XKYRY 7x1.5 SQMM 0.6/1 KV MADE IN IRAN 1399 |  |  |  |  |

Technical approval